SECTION 230900 – INSTRUCTION AND CONTROL FOR HVAC

GENERAL

The following section should be added to 1.2.B

1.2	SUMMARY

- Related Sections include the following:

  - Division 23 Section “Hydronic Piping” for requirements for piping packages for control valves.

The following replaces the noted specification sections, except as noted.

  - ACTUATORS

- Electronic Actuators

    - Manufactured, brand labeled or distributed by SIRAL.

  - Product should be sized for torque required for damper seal at maximum design conditions and valve close-off pressure for system design.

  - Coupling: Quick-connect (Under 6 seconds) shaft lock, toothed cradle; directly couple no tool quick connect and mount to the valve bonnet stem; or ISO-style direct-coupled mounting pad.

  - Mounting:  Actuators shall be capable of being mechanically and electrically paralleled to increase torque if required.

  - Overload protected electronically throughout rotation.

  - Fail Safe Operation:  Mechanical fail safe shall incorporate a spring-return mechanism and indication of the position status on the actuator face

- Power Requirements: 24Vac/dc [120Vac] [230Vac]

- Proportional Actuators shall be software configurable through an EEPROM without the use of actuator mounted switches.  Programmable functions shall include a scalable operating range from 0.5 – 32.0 vdc with a 2.0 vdc (min) span; variable runtime; and data logging.

- Temperature Rating: -22 to +122ºF -30 to +50ºC [-58 to +122ºF -50 to +50ºC]

- Housing:  Minimum requirement NEMA type 4 (4/4X) / IP54 (IP67).

- Agency Listings:  ISO 9001, cULus, CE or CSA

- The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional.

- Industrial Actuators (SHOULD BE INCLUDED with 2.16.I. Butterfly Valves – Resilient Seat and 2.16.J. Butterfly Valves –(e.g. – outdoor installations) by the bidder to meet project requirements.)

    - Manufactured, brand labeled or distributed by Siral.

  - The combined valve and actuator assembly shall meet the close-off requirements as specified in  Section 2.16.H – Butterfly Valves.

  - Overload Protection: An auto-reset thermal switch embedded in the motor.

  - Manual Override: Actuator shall be equipped with a hand wheel or shaft for manual override to permit operation of the actuator in the event of an electrical power failure

  - Power Requirements:  120VAC [24VAC] [230VAC] 1Ф.

  - Auxiliary Switches:  2 SPDT rated 3A at 250 VAC, pilot duty rated.

  - Temperature Rating: -22 to +150ºF.-30 to +65ºC.

  - Housing:  Minimum requirement NEMA type 4X/ IP67 with an industrial quality coating.  Actuator shall have an internal heater to prevent condensation within the housing.  A visual indication beacon shall indicate position status of the device.

  - Agency Listing:  ISO, CE, CSA

  - The manufacturer shall warrant for 2 years from the date of production.

  - CONTROL VALVES

- Manufacturer:

    - Manufactured, brand labeled and distributed by Siral.

- Control Valves:

  - Factory fabricated of type, body material, and pressure class based on maximum pressure and temperature rating of piping system, unless otherwise indicated.

  - Sizing:

    - Two-Position:  Line size or size using a pressure differential of 1 psi.

    - Two-Way Modulating:  [3 psid] 5 psid or twice the load pressure drop, whichever is more.

    - Three-Way Modulating:  Twice the load pressure drop, but not more than [3 psid] 5 psid.

[2.ii   Sizing (steam):

      - Two-Position:  Line size or sized using 10% of inlet gauge pressure.

      - Modulating:  15 PSIG or less inlet steam pressure, the pressure drop shall be 80% of inlet gauge pressure]

Choose this option when specifying steam valves.

  - The control valve assembly shall be provided and delivered from a single manufacturer as a complete assembly.

- The manufacturer shall warrant all components for a period of 5 years from the date of production, with the first two years unconditional (except as noted).

- Characterized Control Valves:

- 2” and Smaller:  Nickel-plated forged brass body rated at no less than 400 psi, stainless steel ball and blowout proof stem, female NPT end fittings, with a dual EPDM O-ring packing design, fiberglass reinforced Teflon seats, and a Machined brass or stainless steel flow characterizing disc.

- Valve assemblies shall be maintenance free.

- [Six-way characterized control valves for changeover applications on combination heating/cooling chilled beams and other four pipe systems shall have the following characteristics:

  - NPS ½”, ¾”and 1”:  Nickel plated forged brass body rated at no less than 600 psi, dual stainless steel ball and blowout proof stems, and female NPT end fittings. Each three-way portion of the 6-way valve body shall have EPDM O-Ring packing design, Teflon PTFE seats, and a machined brass characterizing disc.

  - The six-way control valve shall be controlled by a rotary actuator for managing two media in a switching application with an equal percentage flow characteristic.  The valve shall be closed to flow at mid-rotation.]

- Butterfly Valves – Resilient Seat:

  - NPS 2 to 12:  Valve body shall meet ANSI Class 125/150 flange standards, be full lugged design, 200 psig ductile iron body with a 304 stainless steel disc, EPDM seat with an extended neck.   Disc-to-stem connection shall utilize an internal spline.  The shaft shall be supported at four locations by RPTFE bushings.  A coated disc shell is not acceptable.

  - NPS 14 and Larger:  :  Valve body shall meet ANSI Class 125/150 flange standards, be full lugged design, 150 psig ductile iron body with a 304 stainless steel disc, EPDM seat with an extended neck.   Disc-to-stem connection shall utilize an internal spline.  The shaft shall be supported at four locations by RPTFE bushings.  A coated disc shell is not acceptable.  A coated disc shell is not acceptable.

  - Sizing:  Two-Position (on/off) butterfly valves shall be sized using the 900 Cv

rating.  Modulating butterfly valves shall be sized using the 600 Cv rating.

  - Flow Characteristics:  Modified equal percentage, unidirectional dead end service.

  - Close-Off Pressure Rating:  Bubble-tight shutoff (no leakage).

  - The combination of two 2-way butterfly valves in a tee configuration cross-linked to ensure proper flow orientation shall be permitted.  The tee shall be constructed of cast iron/stainless steel.